Winter Weather Emergency Checklist

THE FOLLOWING CHECKLIST IS INTENDED TO PROVIDE GENERAL INFORMATION NEEDED TO PLAN AND IMPLEMENT AN ADEQUATE RESPONSE TO THIS CATASTROPHIC EXPOSURE. THE PURPOSE OF THIS FORM IS TO HELP PROTECT LIVES, PROPERTY, AND OTHER ASSETS OF THE ORGANIZATION, AND TO ENSURE A PROMPT AND EFFICIENT TRANSITION FROM NORMALCY TO EMERGENCY OPERATIONS AND BACK TO NORMALCY. 

	Pre-Storm Precautions 


General Precautions 
□
Initiate a well-trained Emergency Response Team and emergency action plan. 

□
Designate responsibilities to ensure the plan remains in effect every year. 

□
Develop a list of emergency phone numbers of weather forecasters and contractors, and appoint someone to monitor daily weather reports. 

□
Appoint a designated person to monitor weather reports daily. 

Buildings 
□
Maintain indoor temperatures above 40 F in heated areas to prevent pipe freeze-ups. 
□
Ensure integrity of building shell is in good condition by closing up unnecessary openings. Ensure windows, doors, and skylights are weather-tight. 

□
Inspect remote areas for possible freezing conditions. 
□
Insulate walls and investigate concealed spaces for possible areas lacking insulation. Consider providing temporary interior openings to allow in heat. 

□
Be aware that excessive damage can also be done by hail and flooding. 

Roofs 
□
Institute a roof snow removal program to act immediately after a heavy snow to help reduce excessive snow loads and blocked roof drains from ice.

□
Monitor roof snow levels especially in areas susceptible to large drifts. 

□
Clear all roof and yard drains. Monitor these drains during the storm to make sure they remain clear. 

Parking Lots

□
Look at parking lots for standing water, ice, or snow.  Eliminate as soon as possible.

□
Eliminate any debris (leaf, branches, etc.)

□
Look for water or run off channels that flow towards buildings, redirect as soon as possible. 

Heating Systems

□
Examine the entire heating system components boilers, piping, burners and controls), prior to the cold weather. All deficiencies should be repaired. 

□
Ensure heating equipment is capable of maintaining building temperatures above 40 F at the coldest point within a building (corners, eaves, or areas without heat). 

□
Schedule complete routine inspections for all space heaters to ensure operation. 

□
Ensure adequate clearance is maintained between all heating equipment and combustible walls, floors, partitions, platforms, and stock. 
Fire Protection Equipment/ Domestic Water Lines 
□
Establish a procedure to insure snow is routinely cleared away from hydrants, sprinkler control valves, smoke and heat vents, and other essential equipment, and to make sure this equipment is accessible during emergencies. 

□
Lubricate all sprinkler control valves and locks to permit ease of operation. 

□
Label location of outside sprinkler control valves and hydrants for easy visibility. Also, continue to conduct routine inspections of all sprinkler control valves. 

□
Convert any wet pipe systems in unheated areas to dry or anti-freeze systems. 

□
For dry systems: maintain all dry valve rooms above 40 F, insulate enclosure. Check pitch of piping and drain all low points and auxiliary drains. 

□
Make sure fire pump room is properly heated and the fire pump heating system is operational. 

□
Inspect all gravity tanks for leaks (ice accumulation can create risk of collapse). 

□
Check the water temperature of the fire pump suction tank or gravity tank daily. The tank temperature should be kept above 40 F. 

□
Shut and drain "Close-in-Winter" systems or convert to anti-freeze systems. 

□
Check the specific gravity of all existing anti-freeze systems to see if more concentrate is needed.
□
All wet pipe standpipe systems with piping located in areas subject to freezing should be shut off, drained and tagged. 

□
Connections to all water motor gongs should be properly drained to prevent freezing. 

□
Use a Fire Protection Impairment Kit when shutting off fire protection systems for maintenance. 

□
Water supply, drain, and condensate lines susceptible to freezing (near doorways, uninsulated outside walls, or adjacent to open windows) should be insulated or provided with UL listed heat tracing. 

□
All hoses should be removed from outside water faucets. The faucets should be "frost-proof" self-draining types or isolated indoors and opened to drain. 

Miscellaneous Maintenance 
□
For water-cooled equipment such as pumps and compressors, provide adequate heat or locate in heated enclosures. 

□
Use lubricants on low-temperature applications in equipment such as pumps, blowers and compressors, in areas subjected to freezing temperatures. 

□
For air conditioning, remove water from oil coolers and water jackets, and drain condensers of chilling units. 

□
Check pressure vessel vents, relief valves and safety valves to assure that moving parts are functional. 

	Signed: 

	Dated: 

	Comments: 


NCSIG 11/2012

